## Index
Sheet | Purpose
Index | Loop schedules by area
Scope | All logical points included
Topology | Panel + rack + slot + channel on every data row

## Ensacadeira
Loop Schedule by Area
area: Ensacadeira
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0093 | CV_501_RUN | Retorno em operacao do transportador de alimentacao da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 01 | 01 |  |  | Aux Contact
LP-0098 | LSH_504 | Chave de nivel alto do funil da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 01 | 02 |  |  | Dry Contact
LP-0099 | LSL_504 | Chave de nivel baixo do funil da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 01 | 03 |  |  | Dry Contact
LP-0095 | MTR_502_RUN | Retorno em operacao do motor da maquina de costura | PID-BAG-500 | PNL-BAG-01 | 01 | 01 | 04 |  |  | Aux Contact
LP-0101 | MTR_506_RUN | Retorno em operacao do exaustor do filtro da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 01 | 05 |  |  | Aux Contact
LP-0104 | ALM_508_BEACON | Comando do sinaleiro da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 01 |  |  | 24 Vdc Alarm
LP-0094 | CV_501_START | Comando de partida do transportador de alimentacao da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0096 | MTR_502_START | Comando de partida do motor da maquina de costura | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 03 |  |  | 24 Vdc Run Command
LP-0102 | MTR_506_START | Comando de partida do exaustor do filtro da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 04 |  |  | 24 Vdc Run Command
LP-0108 | SPARE_DO_BAG_01 | Reserva de saida digital da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 05 |  |  | Reserved DO16
LP-0103 | XV_507_CMD | Comando da valvula de corte da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 01 | 02 | 06 |  |  | 24 Vdc Solenoid
LP-0100 | LIT_505 | Transmissor de nivel do funil da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 02 | 01 | 01 | % | 0 .. 100 | 4-20 mA
LP-0105 | PIT_509 | Transmissor de pressao do ar de servico da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 02 | 01 | 02 | bar | 0 .. 8 | 4-20 mA
LP-0106 | TIT_510 | Transmissor de temperatura da seladora | PID-BAG-500 | PNL-BAG-01 | 02 | 01 | 03 | °C | 0 .. 250 | 4-20 mA / temp
LP-0097 | WIT_503 | Transmissor de peso da balanca ensacadeira | PID-BAG-500 | PNL-BAG-01 | 02 | 01 | 04 | kg | 0 .. 50 | 4-20 mA
LP-0107 | CV_511_SPD_REF | Setpoint de velocidade do dosador de rosca da ensacadeira | PID-BAG-500 | PNL-BAG-01 | 03 | 01 | 01 | % | 0 .. 100 | 4-20 mA

## Moega
Loop Schedule by Area
area: Moega
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0025 | CV_211_FLT | Falha do transportador principal da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 01 |  |  | Aux Contact
LP-0024 | CV_211_RUN | Retorno em operacao do transportador principal da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 02 |  |  | Aux Contact
LP-0029 | CV_212_RUN | Retorno em operacao do transportador auxiliar da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 03 |  |  | Aux Contact
LP-0020 | LSH_201 | Chave de nivel alto do silo pulmão da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 04 |  |  | Dry Contact
LP-0021 | LSL_201 | Chave de nivel baixo do silo pulmão da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 05 |  |  | Dry Contact
LP-0035 | MTR_215_RUN | Retorno em operacao do vibrador do silo de transicao | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 06 |  |  | Aux Contact
LP-0034 | XV_214_FB | Retorno de posicao da valvula de alivio do silo de transicao | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 07 |  |  | Dry Contact
LP-0032 | ZS_213_OPEN | Fim de curso aberto da comporta desviadora da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 01 | 08 |  |  | Dry Contact
LP-0039 | ALM_220_HORN | Comando da buzina de alarme da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 01 |  |  | 24 Vdc Alarm
LP-0026 | CV_211_START | Comando de partida do transportador principal da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0030 | CV_212_START | Comando de partida do transportador auxiliar da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 03 |  |  | 24 Vdc Run Command
LP-0036 | MTR_215_START | Comando de partida do vibrador do silo de transicao | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 04 |  |  | 24 Vdc Run Command
LP-0033 | XV_214_CMD | Comando da valvula de alivio do silo de transicao | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 05 |  |  | 24 Vdc Solenoid
LP-0031 | YV_213_CMD | Comando da comporta desviadora da moega | PID-MOG-200 | PNL-MOG-01 | 01 | 02 | 06 |  |  | 24 Vdc Solenoid
LP-0027 | CV_211_SPD_FBK | Referencia real de velocidade do transportador principal da moega | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 01 | Hz | 0 .. 60 | 4-20 mA
LP-0023 | FIT_203 | Transmissor de vazao da calha vibratoria da moega | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 02 | t/h | 0 .. 80 | 4-20 mA
LP-0022 | LIT_202 | Transmissor de nivel do silo pulmão da moega | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 03 | % | 0 .. 100 | 4-20 mA
LP-0037 | PIT_216 | Transmissor de pressao da linha de despoeiramento | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 04 | mbar | -50 .. 50 | 4-20 mA
LP-0041 | SPARE_AI_MOG_01 | Reserva analogica no rack de moega | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 05 |  |  | Reserved AI8
LP-0038 | TIT_217 | Transmissor de temperatura do mancal do transportador principal | PID-MOG-200 | PNL-MOG-01 | 02 | 01 | 06 | °C | 0 .. 120 | 4-20 mA / temp
LP-0028 | CV_211_SPD_REF | Setpoint de velocidade do transportador principal da moega | PID-MOG-200 | PNL-MOG-01 | 03 | 01 | 01 | Hz | 0 .. 60 | 4-20 mA
LP-0040 | FCV_219_OUT | Setpoint da valvula de recirculacao de po | PID-MOG-200 | PNL-MOG-01 | 03 | 01 | 02 | % | 0 .. 100 | 4-20 mA

## Processo
Loop Schedule by Area
area: Processo
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0067 | LSH_401 | Chave de nivel alto do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 01 |  |  | Dry Contact
LP-0068 | LSL_401 | Chave de nivel baixo do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 02 |  |  | Dry Contact
LP-0076 | MTR_411_FLT | Falha do agitador principal do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 03 |  |  | Aux Contact
LP-0075 | MTR_411_RUN | Retorno em operacao do agitador principal do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 04 |  |  | Aux Contact
LP-0080 | PMP_412_RUN | Retorno em operacao do bomba de recirculacao de processo | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 05 |  |  | Aux Contact
LP-0091 | SPARE_DI_PRC_01 | Reserva de entrada digital do processo | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 06 |  |  | Reserved DI16
LP-0086 | UV_415_HEALTHY | Saude do modulo UV da linha de sanitizacao | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 07 |  |  | Dry Contact
LP-0083 | XV_413_FB | Retorno de posicao da valvula de entrada de agua de processo | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 08 |  |  | Dry Contact
LP-0085 | XV_414_FB | Retorno de posicao da valvula de descarga do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 01 | 09 |  |  | Dry Contact
LP-0090 | ALM_418_HORN | Comando da buzina de alarme do processo | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 01 |  |  | 24 Vdc Alarm
LP-0077 | MTR_411_START | Comando de partida do agitador principal do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0081 | PMP_412_START | Comando de partida do bomba de recirculacao de processo | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 03 |  |  | 24 Vdc Run Command
LP-0087 | UV_415_ENABLE | Comando de habilitacao do modulo UV | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 04 |  |  | 24 Vdc Enable
LP-0082 | XV_413_CMD | Comando da valvula de entrada de agua de processo | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 05 |  |  | 24 Vdc Solenoid
LP-0084 | XV_414_CMD | Comando da valvula de descarga do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 01 | 02 | 06 |  |  | 24 Vdc Solenoid
LP-0074 | AIT_407 | Transmissor de condutividade da linha de lavagem | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 01 | mS/cm | 0 .. 20 | 4-20 mA
LP-0073 | FIT_406 | Transmissor de vazao da linha de dosagem | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 02 | m3/h | 0 .. 25 | 4-20 mA
LP-0069 | LIT_402 | Transmissor de nivel do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 03 | % | 0 .. 100 | 4-20 mA
LP-0078 | MTR_411_SPD_FBK | Referencia real de velocidade do agitador principal do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 04 | % | 0 .. 100 | 4-20 mA
LP-0072 | PHIT_405 | Transmissor de pH da linha de preparo | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 05 | pH | 0 .. 14 | 4-20 mA
LP-0070 | PIT_403 | Transmissor de pressao do manifold de processo | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 06 | bar | 0 .. 10 | 4-20 mA
LP-0071 | TIT_404 | Transmissor de temperatura do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 02 | 01 | 07 | °C | 0 .. 120 | 4-20 mA / temp
LP-0088 | FCV_416_OUT | Setpoint da valvula de controle de vazao de processo | PID-PRC-400 | PNL-PRC-01 | 03 | 01 | 01 | % | 0 .. 100 | 4-20 mA
LP-0079 | MTR_411_SPD_REF | Setpoint de velocidade do agitador principal do tanque de mistura | PID-PRC-400 | PNL-PRC-01 | 03 | 01 | 02 | % | 0 .. 100 | 4-20 mA
LP-0089 | PCV_417_OUT | Setpoint da valvula de controle de pressao de processo | PID-PRC-400 | PNL-PRC-01 | 03 | 01 | 03 | % | 0 .. 100 | 4-20 mA
LP-0092 | SPARE_AO_PRC_02 | Reserva analogica de saida do processo | PID-PRC-400 | PNL-PRC-01 | 03 | 01 | 04 |  |  | Reserved AO8

## Recebimento
Loop Schedule by Area
area: Recebimento
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0007 | CV_111_FLT | Falha do rosca de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 01 |  |  | Aux Contact
LP-0006 | CV_111_RUN | Retorno em operacao do rosca de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 02 |  |  | Aux Contact
LP-0003 | LSH_101 | Chave de nivel alto da moega rodoviaria | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 03 |  |  | Dry Contact
LP-0004 | LSL_101 | Chave de nivel baixo da moega rodoviaria | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 04 |  |  | Dry Contact
LP-0011 | MTR_112_RUN | Retorno em operacao do exaustor do filtro do recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 05 |  |  | Aux Contact
LP-0019 | SPARE_DI_RCV_01 | Reserva de entrada digital no painel de recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 06 |  |  | Reserved DI16
LP-0002 | XV_101_FB | Retorno de posicao da comporta de descarga do fosso | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 07 |  |  | Dry Contact
LP-0016 | YV_115_FB | Retorno de posicao da valvula desviadora de amostragem | PID-RCV-100 | PNL-RCV-01 | 01 | 01 | 08 |  |  | Dry Contact
LP-0008 | CV_111_START | Comando de partida do rosca de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 02 | 01 |  |  | 24 Vdc Run Command
LP-0012 | MTR_112_START | Comando de partida do exaustor do filtro do recebimento | PID-RCV-100 | PNL-RCV-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0018 | PMP_117_START | Comando de partida da bomba de lavagem | PID-RCV-100 | PNL-RCV-01 | 01 | 02 | 03 |  |  | 24 Vdc Run Command
LP-0001 | XV_101_CMD | Comando da comporta de descarga do fosso | PID-RCV-100 | PNL-RCV-01 | 01 | 02 | 04 |  |  | 24 Vdc Solenoid
LP-0015 | YV_115_CMD | Comando da valvula desviadora de amostragem | PID-RCV-100 | PNL-RCV-01 | 01 | 02 | 05 |  |  | 24 Vdc Solenoid
LP-0009 | CV_111_SPD_FBK | Referencia real de velocidade do rosca de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 02 | 01 | 01 | % | 0 .. 100 | 4-20 mA
LP-0014 | FIT_114 | Transmissor de vazao de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 02 | 01 | 02 | t/h | 0 .. 60 | 4-20 mA
LP-0005 | LIT_101 | Transmissor de nivel da moega rodoviaria | PID-RCV-100 | PNL-RCV-01 | 02 | 01 | 03 | % | 0 .. 100 | 4-20 mA
LP-0013 | PIT_113 | Transmissor de pressao da linha de fluidizacao | PID-RCV-100 | PNL-RCV-01 | 02 | 01 | 04 | bar | 0 .. 6 | 4-20 mA
LP-0010 | CV_111_SPD_REF | Setpoint de velocidade do rosca de descarga do recebimento | PID-RCV-100 | PNL-RCV-01 | 03 | 01 | 01 | % | 0 .. 100 | 4-20 mA
LP-0017 | FCV_116_OUT | Setpoint da valvula de dosagem de agua | PID-RCV-100 | PNL-RCV-01 | 03 | 01 | 02 | % | 0 .. 100 | 4-20 mA

## Transporte
Loop Schedule by Area
area: Transporte
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0051 | BE_303_FLT | Falha do elevador de canecas | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 01 |  |  | Aux Contact
LP-0050 | BE_303_RUN | Retorno em operacao do elevador de canecas | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 02 |  |  | Aux Contact
LP-0043 | CV_301_FLT | Falha do transportador de correia principal | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 03 |  |  | Aux Contact
LP-0042 | CV_301_RUN | Retorno em operacao do transportador de correia principal | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 04 |  |  | Aux Contact
LP-0048 | CV_302_FLT | Falha do transportador de correia secundario | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 05 |  |  | Aux Contact
LP-0047 | CV_302_RUN | Retorno em operacao do transportador de correia secundario | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 06 |  |  | Aux Contact
LP-0054 | XV_304_FB | Retorno de posicao da valvula guilhotina do chute A | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 07 |  |  | Dry Contact
LP-0056 | YV_305_FB | Retorno de posicao da valvula desviadora do chute B | PID-TRN-300 | MCC-TRN-01 | 01 | 01 | 08 |  |  | Dry Contact
LP-0061 | ALM_314_BEACON | Comando do sinaleiro do transporte | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 01 |  |  | 24 Vdc Alarm
LP-0052 | BE_303_START | Comando de partida do elevador de canecas | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0044 | CV_301_START | Comando de partida do transportador de correia principal | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 03 |  |  | 24 Vdc Run Command
LP-0049 | CV_302_START | Comando de partida do transportador de correia secundario | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 04 |  |  | 24 Vdc Run Command
LP-0065 | SPARE_DO_TRN_01 | Reserva de saida digital do transporte | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 05 |  |  | Reserved DO16
LP-0062 | SV_315_CMD | Comando da valvula de spray de mitigacao de poeira | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 06 |  |  | 24 Vdc Solenoid
LP-0053 | XV_304_CMD | Comando da valvula guilhotina do chute A | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 07 |  |  | 24 Vdc Solenoid
LP-0055 | YV_305_CMD | Comando da valvula desviadora do chute B | PID-TRN-300 | MCC-TRN-01 | 01 | 02 | 08 |  |  | 24 Vdc Solenoid
LP-0045 | CV_301_SPD_FBK | Referencia real de velocidade do transportador de correia principal | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 01 | Hz | 0 .. 60 | 4-20 mA
LP-0057 | FIT_307 | Transmissor de vazao da linha de transporte principal | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 02 | t/h | 0 .. 120 | 4-20 mA
LP-0059 | PIT_309 | Transmissor de pressao da linha de transporte pneumático | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 03 | bar | 0 .. 2.5 | 4-20 mA
LP-0066 | SPARE_AI_TRN_02 | Reserva analogica do transporte | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 04 |  |  | Reserved AI8
LP-0060 | TIT_310 | Transmissor de temperatura do mancal do elevador | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 05 | °C | 0 .. 120 | 4-20 mA / temp
LP-0058 | WIT_308 | Transmissor de carga da balanca integradora | PID-TRN-300 | MCC-TRN-01 | 02 | 01 | 06 | t/h | 0 .. 150 | 4-20 mA
LP-0046 | CV_301_SPD_REF | Setpoint de velocidade do transportador de correia principal | PID-TRN-300 | MCC-TRN-01 | 03 | 01 | 01 | Hz | 0 .. 60 | 4-20 mA
LP-0064 | DMPR_313_POS_REF | Setpoint do damper da exaustao do transporte | PID-TRN-300 | MCC-TRN-01 | 03 | 01 | 02 | % | 0 .. 100 | 4-20 mA
LP-0063 | FCV_312_OUT | Setpoint da valvula de controle de vazao do bypass | PID-TRN-300 | MCC-TRN-01 | 03 | 01 | 03 | % | 0 .. 100 | 4-20 mA

## Utilidades
Loop Schedule by Area
area: Utilidades
Loop | Tag | Service | P&ID | Panel | Rack | Slot | Ch | Unit | Range | Signal
LP-0110 | COMP_601_FLT | Falha do compressor principal | PID-UTL-600 | PNL-UTL-01 | 01 | 01 | 01 |  |  | Aux Contact
LP-0109 | COMP_601_RUN | Retorno em operacao do compressor principal | PID-UTL-600 | PNL-UTL-01 | 01 | 01 | 02 |  |  | Aux Contact
LP-0117 | PMP_606_RUN | Retorno em operacao do bomba de recirculacao da torre de resfriamento | PID-UTL-600 | PNL-UTL-01 | 01 | 01 | 03 |  |  | Aux Contact
LP-0116 | XV_605_FB | Retorno de posicao da valvula de bloqueio do header de ar | PID-UTL-600 | PNL-UTL-01 | 01 | 01 | 04 |  |  | Dry Contact
LP-0111 | COMP_601_START | Comando de partida do compressor principal | PID-UTL-600 | PNL-UTL-01 | 01 | 02 | 01 |  |  | 24 Vdc Run Command
LP-0118 | PMP_606_START | Comando de partida do bomba de recirculacao da torre de resfriamento | PID-UTL-600 | PNL-UTL-01 | 01 | 02 | 02 |  |  | 24 Vdc Run Command
LP-0115 | XV_605_CMD | Comando da valvula de bloqueio do header de ar | PID-UTL-600 | PNL-UTL-01 | 01 | 02 | 03 |  |  | 24 Vdc Solenoid
LP-0113 | FIT_603 | Transmissor de vazao de agua industrial | PID-UTL-600 | PNL-UTL-01 | 02 | 01 | 01 | m3/h | 0 .. 40 | 4-20 mA
LP-0112 | PIT_602 | Transmissor de pressao do header de ar comprimido | PID-UTL-600 | PNL-UTL-01 | 02 | 01 | 02 | bar | 0 .. 10 | 4-20 mA
LP-0120 | SPARE_AI_UTL_01 | Reserva analogica de utilidades | PID-UTL-600 | PNL-UTL-01 | 02 | 01 | 03 |  |  | Reserved AI8
LP-0114 | TIT_604 | Transmissor de temperatura da linha de agua gelada | PID-UTL-600 | PNL-UTL-01 | 02 | 01 | 04 | °C | 0 .. 30 | 4-20 mA / temp
LP-0119 | PCV_607_OUT | Setpoint da valvula de controle de pressao do ar | PID-UTL-600 | PNL-UTL-01 | 03 | 01 | 01 | % | 0 .. 100 | 4-20 mA

## area Summary
area | Points | DI | DO | AI | AO | SPARE
Ensacadeira | 16 | 5 | 5 | 4 | 1 | 1
Moega | 22 | 8 | 6 | 5 | 2 | 1
Processo | 26 | 8 | 6 | 7 | 3 | 2
Recebimento | 19 | 7 | 5 | 4 | 2 | 1
Transporte | 25 | 8 | 7 | 5 | 3 | 2
Utilidades | 12 | 4 | 3 | 3 | 1 | 1