## Compact IO
Point Ref | Location | Card Position | Type | Signal | Tag | Service | Panel | Field Wiring | Range / Unit | Remarks
MCC-TRN-01::BE_303_FLT | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 01 / Torre do elevador | R01-S01-CH01 | DI | Aux Contact | BE_303_FLT | bucket elevator fault feedback | MCC-TRN-01 | JB-TRN-02 / X1-10
MCC-TRN-01::BE_303_RUN | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 02 / Torre do elevador | Rack 1 / Slot 1 / Ch 02 | DI | Aux Contact | BE_303_RUN | bucket elevator running feedback | MCC-TRN-01 | JB-TRN-01 / X3-09
MCC-TRN-01::CV_301_FLT | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 03 / Galeria principal de transporte | MCC-TRN-01.R1.S1.C3 | DI | Aux Contact | CV_301_FLT | main belt conveyor fault feedback | MCC-TRN-01 | JB-TRN-02 / X2-02 |  | Signal sourced from the drive.
MCC-TRN-01::CV_301_RUN | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 04 / Galeria principal de transporte | R01-S01-CH04 | DI | Aux Contact | CV_301_RUN | main belt conveyor running feedback | MCC-TRN-01 | JB-TRN-01 / X1-01
MCC-TRN-01::CV_302_FLT | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 05 / Galeria secundaria de transporte | Rack 1 / Slot 1 / Ch 05 | DI | Aux Contact | CV_302_FLT | secondary belt conveyor fault feedback | MCC-TRN-01 | JB-TRN-03 / X1-07
MCC-TRN-01::CV_302_RUN | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 06 / Galeria secundaria de transporte | MCC-TRN-01.R1.S1.C6 | DI | Aux Contact | CV_302_RUN | secondary belt conveyor running feedback | MCC-TRN-01 | JB-TRN-02 / X3-06
MCC-TRN-01::XV_304_FB | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 07 / Chute de transferencia A | R01-S01-CH07 | DI | Dry Contact | XV_304_FB | chute A knife gate valve position feedback | MCC-TRN-01 | JB-TRN-01 / X1-13
MCC-TRN-01::YV_305_FB | MCC-TRN-01 / Rack 1 / Slot 1 / Ch 08 / Chute de transferencia B | Rack 1 / Slot 1 / Ch 08 | DI | Dry Contact | YV_305_FB | chute B diverter valve position feedback | MCC-TRN-01 | JB-TRN-03 / X3-15
MCC-TRN-01::ALM_314_BEACON | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 01 / Passarela principal de transporte | R01-S02-CH01 | DO | 24 Vdc Alarm | ALM_314_BEACON | Conveying beacon command | MCC-TRN-01 | JB-TRN-04 / X2-04
MCC-TRN-01::BE_303_START | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 02 / Torre do elevador | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | BE_303_START | bucket elevator start command | MCC-TRN-01 | JB-TRN-03 / X2-11
MCC-TRN-01::CV_301_START | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 03 / Galeria principal de transporte | MCC-TRN-01.R1.S2.C3 | DO | 24 Vdc Run Command | CV_301_START | main belt conveyor start command | MCC-TRN-01 | JB-TRN-03 / X3-03 |  | Command released by process interlock.
MCC-TRN-01::CV_302_START | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 04 / Galeria secundaria de transporte | R01-S02-CH04 | DO | 24 Vdc Run Command | CV_302_START | secondary belt conveyor start command | MCC-TRN-01 | JB-TRN-04 / X2-08
MCC-TRN-01::SPARE_DO_TRN_01 | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 05 / Galeria de transporte / trecho principal | Rack 1 / Slot 2 / Ch 05 | SPARE | Reserved DO16 | SPARE_DO_TRN_01 | Reserved digital output on conveying panel | MCC-TRN-01 | JB-TRN-04 / X3-08 |  | Available for future extra siren.
MCC-TRN-01::SV_315_CMD | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 06 / Chute de transferencia principal | MCC-TRN-01.R1.S2.C6 | DO | 24 Vdc Solenoid | SV_315_CMD | Dust suppression spray valve command | MCC-TRN-01 | JB-TRN-01 / X3-05
MCC-TRN-01::XV_304_CMD | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 07 / Chute de transferencia A | R01-S02-CH07 | DO | 24 Vdc Solenoid | XV_304_CMD | chute A knife gate valve command | MCC-TRN-01 | JB-TRN-04 / X3-12
MCC-TRN-01::YV_305_CMD | MCC-TRN-01 / Rack 1 / Slot 2 / Ch 08 / Chute de transferencia B | Rack 1 / Slot 2 / Ch 08 | DO | 24 Vdc Solenoid | YV_305_CMD | chute B diverter valve command | MCC-TRN-01 | JB-TRN-02 / X2-14
MCC-TRN-01::CV_301_SPD_FBK | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 01 / Galeria principal de transporte | R02-S01-CH01 | AI | 4-20 mA | CV_301_SPD_FBK | main belt conveyor actual speed feedback | MCC-TRN-01 | JB-TRN-04 / X1-04 | 0 .. 60 Hz
MCC-TRN-01::FIT_307 | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 02 / Chute de transferencia principal | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | FIT_307 | Main conveying line flow transmitter | MCC-TRN-01 | JB-TRN-04 / X1-16 | 0 .. 120 t/h
MCC-TRN-01::PIT_309 | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 03 / Coletor da linha pneumática | MCC-TRN-01.R2.S1.C3 | AI | 4-20 mA | PIT_309 | Pneumatic conveying line pressure transmitter | MCC-TRN-01 | JB-TRN-02 / X3-02 | 0 .. 2.5 bar
MCC-TRN-01::SPARE_AI_TRN_02 | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 04 / Galeria de transporte / trecho principal | R02-S01-CH04 | SPARE | Reserved AI8 | SPARE_AI_TRN_02 | Reserved analog input on conveying panel | MCC-TRN-01 | JB-TRN-01 / X1-09 |  | Channel reserved for vibration monitor.
MCC-TRN-01::TIT_310 | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 05 / Mancal superior do elevador | Rack 2 / Slot 1 / Ch 05 | AI | 4-20 mA / temp | TIT_310 | Bucket elevator bearing temperature transmitter | MCC-TRN-01 | JB-TRN-03 / X1-03 | 0 .. 120 °C
MCC-TRN-01::WIT_308 | MCC-TRN-01 / Rack 2 / Slot 1 / Ch 06 / Balanca integradora do CV_301 | MCC-TRN-01.R2.S1.C6 | AI | 4-20 mA | WIT_308 | Belt scale load transmitter | MCC-TRN-01 | JB-TRN-01 / X2-01 | 0 .. 150 t/h
MCC-TRN-01::CV_301_SPD_REF | MCC-TRN-01 / Rack 3 / Slot 1 / Ch 01 / Galeria principal de transporte | R03-S01-CH01 | AO | 4-20 mA | CV_301_SPD_REF | main belt conveyor speed setpoint | MCC-TRN-01 | JB-TRN-01 / X2-05 | 0 .. 60 Hz
MCC-TRN-01::DMPR_313_POS_REF | MCC-TRN-01 / Rack 3 / Slot 1 / Ch 02 / Duto de exaustao do transporte | Rack 3 / Slot 1 / Ch 02 | AO | 4-20 mA | DMPR_313_POS_REF | Conveying exhaust damper position setpoint | MCC-TRN-01 | JB-TRN-03 / X2-07 | 0 .. 100 %
MCC-TRN-01::FCV_312_OUT | MCC-TRN-01 / Rack 3 / Slot 1 / Ch 03 / Linha de bypass do transporte | MCC-TRN-01.R3.S1.C3 | AO | 4-20 mA | FCV_312_OUT | Bypass flow control valve setpoint | MCC-TRN-01 | JB-TRN-02 / X1-06 | 0 .. 100 %
PNL-BAG-01::CV_501_RUN | PNL-BAG-01 / Rack 1 / Slot 1 / Ch 01 / Entrada da ensacadeira | R01-S01-CH01 | DI | Aux Contact | CV_501_RUN | bagger feed conveyor running feedback | PNL-BAG-01 | JB-BAG-01 / X1-01
PNL-BAG-01::LSH_504 | PNL-BAG-01 / Rack 1 / Slot 1 / Ch 02 / Funil da ensacadeira | Rack 1 / Slot 1 / Ch 02 | DI | Dry Contact | LSH_504 | Bagger hopper high level switch | PNL-BAG-01 | JB-BAG-02 / X3-06
PNL-BAG-01::LSL_504 | PNL-BAG-01 / Rack 1 / Slot 1 / Ch 03 / Funil da ensacadeira | PNL-BAG-01.R1.S1.C3 | DI | Dry Contact | LSL_504 | Bagger hopper low level switch | PNL-BAG-01 | JB-BAG-03 / X1-07
PNL-BAG-01::MTR_502_RUN | PNL-BAG-01 / Rack 1 / Slot 1 / Ch 04 / Cabecote da costura | R01-S01-CH04 | DI | Aux Contact | MTR_502_RUN | bag sewing machine motor running feedback | PNL-BAG-01 | JB-BAG-03 / X3-03
PNL-BAG-01::MTR_506_RUN | PNL-BAG-01 / Rack 1 / Slot 1 / Ch 05 / Filtro de mangas da ensacadeira | Rack 1 / Slot 1 / Ch 05 | DI | Aux Contact | MTR_506_RUN | bagger dust collector fan running feedback | PNL-BAG-01 | JB-BAG-01 / X3-09
PNL-BAG-01::ALM_508_BEACON | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 01 / Coluna de sinaleiro da ensacadeira | R01-S02-CH01 | DO | 24 Vdc Alarm | ALM_508_BEACON | Bagging line beacon command | PNL-BAG-01 | JB-BAG-04 / X3-12
PNL-BAG-01::CV_501_START | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 02 / Entrada da ensacadeira | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | CV_501_START | bagger feed conveyor start command | PNL-BAG-01 | JB-BAG-02 / X2-02
PNL-BAG-01::MTR_502_START | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 03 / Cabecote da costura | PNL-BAG-01.R1.S2.C3 | DO | 24 Vdc Run Command | MTR_502_START | bag sewing machine motor start command | PNL-BAG-01 | JB-BAG-04 / X1-04
PNL-BAG-01::MTR_506_START | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 04 / Filtro de mangas da ensacadeira | R01-S02-CH04 | DO | 24 Vdc Run Command | MTR_506_START | bagger dust collector fan start command | PNL-BAG-01 | JB-BAG-02 / X1-10
PNL-BAG-01::SPARE_DO_BAG_01 | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 05 / Linha de ensaque / corredor de maquinas | Rack 1 / Slot 2 / Ch 05 | SPARE | Reserved DO16 | SPARE_DO_BAG_01 | Reserved digital output on bagging panel | PNL-BAG-01 | JB-BAG-04 / X1-16 |  | Free channel for future stack light.
PNL-BAG-01::XV_507_CMD | PNL-BAG-01 / Rack 1 / Slot 2 / Ch 06 / Linha de enchimento | PNL-BAG-01.R1.S2.C6 | DO | 24 Vdc Solenoid | XV_507_CMD | Bagger cutoff valve command | PNL-BAG-01 | JB-BAG-03 / X2-11
PNL-BAG-01::LIT_505 | PNL-BAG-01 / Rack 2 / Slot 1 / Ch 01 / Funil da ensacadeira | R02-S01-CH01 | AI | 4-20 mA | LIT_505 | Bagger hopper level transmitter | PNL-BAG-01 | JB-BAG-04 / X2-08 | 0 .. 100 %
PNL-BAG-01::PIT_509 | PNL-BAG-01 / Rack 2 / Slot 1 / Ch 02 / Linha de ar comprimido da ensacadeira | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | PIT_509 | Bagging service air pressure transmitter | PNL-BAG-01 | JB-BAG-01 / X1-13 | 0 .. 8 bar
PNL-BAG-01::TIT_510 | PNL-BAG-01 / Rack 2 / Slot 1 / Ch 03 / Cabecote da seladora | PNL-BAG-01.R2.S1.C3 | AI | 4-20 mA / temp | TIT_510 | Sealer temperature transmitter | PNL-BAG-01 | JB-BAG-02 / X2-14 | 0 .. 250 °C
PNL-BAG-01::WIT_503 | PNL-BAG-01 / Rack 2 / Slot 1 / Ch 04 / Balanca da ensacadeira | R02-S01-CH04 | AI | 4-20 mA | WIT_503 | Bagging scale weight transmitter | PNL-BAG-01 | JB-BAG-01 / X2-05 | 0 .. 50 kg
PNL-BAG-01::CV_511_SPD_REF | PNL-BAG-01 / Rack 3 / Slot 1 / Ch 01 / Dosador de rosca da ensacadeira | R03-S01-CH01 | AO | 4-20 mA | CV_511_SPD_REF | Bagger screw feeder speed setpoint | PNL-BAG-01 | JB-BAG-03 / X3-15 | 0 .. 100 %
PNL-MOG-01::CV_211_FLT | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 01 / Galeria de transferencia da moega | R01-S01-CH01 | DI | Aux Contact | CV_211_FLT | hopper main conveyor fault feedback | PNL-MOG-01 | JB-MOG-02 / X3-06 |  | Signal sourced from the drive.
PNL-MOG-01::CV_211_RUN | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 02 / Galeria de transferencia da moega | Rack 1 / Slot 1 / Ch 02 | DI | Aux Contact | CV_211_RUN | hopper main conveyor running feedback | PNL-MOG-01 | JB-MOG-01 / X2-05
PNL-MOG-01::CV_212_RUN | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 03 / Galeria de transferencia da moega | PNL-MOG-01.R1.S1.C3 | DI | Aux Contact | CV_212_RUN | hopper auxiliary conveyor running feedback | PNL-MOG-01 | JB-MOG-02 / X1-10
PNL-MOG-01::LSH_201 | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 04 / Silo pulmão da moega | R01-S01-CH04 | DI | Dry Contact | LSH_201 | Hopper buffer bin high level switch | PNL-MOG-01 | JB-MOG-01 / X1-01
PNL-MOG-01::LSL_201 | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 05 / Silo pulmão da moega | Rack 1 / Slot 1 / Ch 05 | DI | Dry Contact | LSL_201 | Hopper buffer bin low level switch | PNL-MOG-01 | JB-MOG-02 / X2-02
PNL-MOG-01::MTR_215_RUN | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 06 / Cone inferior do silo de transicao | PNL-MOG-01.R1.S1.C6 | DI | Aux Contact | MTR_215_RUN | transition bin vibrator running feedback | PNL-MOG-01 | JB-MOG-04 / X1-16
PNL-MOG-01::XV_214_FB | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 07 / Silo de transicao da moega | R01-S01-CH07 | DI | Dry Contact | XV_214_FB | transition bin vent valve position feedback | PNL-MOG-01 | JB-MOG-03 / X3-15
PNL-MOG-01::ZS_213_OPEN | PNL-MOG-01 / Rack 1 / Slot 1 / Ch 08 / Bifurcacao de descarga da moega | Rack 1 / Slot 1 / Ch 08 | DI | Dry Contact | ZS_213_OPEN | Hopper diverter gate open limit switch | PNL-MOG-01 | JB-MOG-01 / X1-13
PNL-MOG-01::ALM_220_HORN | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 01 / Passarela da moega | R01-S02-CH01 | DO | 24 Vdc Alarm | ALM_220_HORN | Hopper alarm horn command | PNL-MOG-01 | JB-MOG-04 / X2-04
PNL-MOG-01::CV_211_START | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 02 / Galeria de transferencia da moega | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | CV_211_START | hopper main conveyor start command | PNL-MOG-01 | JB-MOG-03 / X1-07 |  | Command released by process interlock.
PNL-MOG-01::CV_212_START | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 03 / Galeria de transferencia da moega | PNL-MOG-01.R1.S2.C3 | DO | 24 Vdc Run Command | CV_212_START | hopper auxiliary conveyor start command | PNL-MOG-01 | JB-MOG-03 / X2-11
PNL-MOG-01::MTR_215_START | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 04 / Cone inferior do silo de transicao | R01-S02-CH04 | DO | 24 Vdc Run Command | MTR_215_START | transition bin vibrator start command | PNL-MOG-01 | JB-MOG-01 / X2-01
PNL-MOG-01::XV_214_CMD | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 05 / Silo de transicao da moega | Rack 1 / Slot 2 / Ch 05 | DO | 24 Vdc Solenoid | XV_214_CMD | transition bin vent valve command | PNL-MOG-01 | JB-MOG-02 / X2-14
PNL-MOG-01::YV_213_CMD | PNL-MOG-01 / Rack 1 / Slot 2 / Ch 06 / Bifurcacao de descarga da moega | PNL-MOG-01.R1.S2.C6 | DO | 24 Vdc Solenoid | YV_213_CMD | Hopper diverter gate command | PNL-MOG-01 | JB-MOG-04 / X3-12
PNL-MOG-01::CV_211_SPD_FBK | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 01 / Galeria de transferencia da moega | R02-S01-CH01 | AI | 4-20 mA | CV_211_SPD_FBK | hopper main conveyor actual speed feedback | PNL-MOG-01 | JB-MOG-04 / X2-08 | 0 .. 60 Hz
PNL-MOG-01::FIT_203 | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 02 / Calha vibratoria da moega | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | FIT_203 | Hopper feeder flow transmitter | PNL-MOG-01 | JB-MOG-04 / X1-04 | 0 .. 80 t/h
PNL-MOG-01::LIT_202 | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 03 / Silo pulmão da moega | PNL-MOG-01.R2.S1.C3 | AI | 4-20 mA | LIT_202 | Hopper buffer bin level transmitter | PNL-MOG-01 | JB-MOG-03 / X3-03 | 0 .. 100 %
PNL-MOG-01::PIT_216 | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 04 / Coletor de despoeiramento da moega | R02-S01-CH04 | AI | 4-20 mA | PIT_216 | Dust collection line pressure transmitter | PNL-MOG-01 | JB-MOG-02 / X3-02 | -50 .. 50 mbar
PNL-MOG-01::SPARE_AI_MOG_01 | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 05 / Predio da moega / nivel operacional | Rack 2 / Slot 1 / Ch 05 | SPARE | Reserved AI8 | SPARE_AI_MOG_01 | Reserved analog input on hopper rack | PNL-MOG-01 | JB-MOG-02 / X1-06 |  | Provisioned for future vibration transmitter.
PNL-MOG-01::TIT_217 | PNL-MOG-01 / Rack 2 / Slot 1 / Ch 06 / Mancal motriz do CV_211 | PNL-MOG-01.R2.S1.C6 | AI | 4-20 mA / temp | TIT_217 | Main conveyor bearing temperature transmitter | PNL-MOG-01 | JB-MOG-03 / X1-03 | 0 .. 120 °C
PNL-MOG-01::CV_211_SPD_REF | PNL-MOG-01 / Rack 3 / Slot 1 / Ch 01 / Galeria de transferencia da moega | R03-S01-CH01 | AO | 4-20 mA | CV_211_SPD_REF | hopper main conveyor speed setpoint | PNL-MOG-01 | JB-MOG-01 / X3-09 | 0 .. 60 Hz
PNL-MOG-01::FCV_219_OUT | PNL-MOG-01 / Rack 3 / Slot 1 / Ch 02 / Linha de recirculacao de po | Rack 3 / Slot 1 / Ch 02 | AO | 4-20 mA | FCV_219_OUT | Dust recirculation control valve setpoint | PNL-MOG-01 | JB-MOG-01 / X3-05 | 0 .. 100 %
PNL-PRC-01::LSH_401 | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 01 / Tanque de mistura TQ_401 | R01-S01-CH01 | DI | Dry Contact | LSH_401 | Mix tank high level switch | PNL-PRC-01 | JB-PRC-01 / X1-01
PNL-PRC-01::LSL_401 | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 02 / Tanque de mistura TQ_401 | Rack 1 / Slot 1 / Ch 02 | DI | Dry Contact | LSL_401 | Mix tank low level switch | PNL-PRC-01 | JB-PRC-02 / X2-02
PNL-PRC-01::MTR_411_FLT | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 03 / Topo do tanque de mistura | PNL-PRC-01.R1.S1.C3 | DI | Aux Contact | MTR_411_FLT | mix tank main agitator fault feedback | PNL-PRC-01 | JB-PRC-02 / X1-10 |  | Signal sourced from the drive.
PNL-PRC-01::MTR_411_RUN | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 04 / Topo do tanque de mistura | R01-S01-CH04 | DI | Aux Contact | MTR_411_RUN | mix tank main agitator running feedback | PNL-PRC-01 | JB-PRC-01 / X3-09
PNL-PRC-01::PMP_412_RUN | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 05 / Skid de recirculacao do processo | Rack 1 / Slot 1 / Ch 05 | DI | Aux Contact | PMP_412_RUN | process recirculation pump running feedback | PNL-PRC-01 | JB-PRC-02 / X2-14
PNL-PRC-01::SPARE_DI_PRC_01 | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 06 / Sala de processo / plataforma principal | PNL-PRC-01.R1.S1.C6 | SPARE | Reserved DI16 | SPARE_DI_PRC_01 | Reserved digital input on process panel | PNL-PRC-01 | JB-PRC-01 / X1-09 |  | Reserved for future pressure switch.
PNL-PRC-01::UV_415_HEALTHY | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 07 / Skid de sanitizacao | R01-S01-CH07 | DI | Dry Contact | UV_415_HEALTHY | Sanitizing line UV module healthy status | PNL-PRC-01 | JB-PRC-04 / X2-04
PNL-PRC-01::XV_413_FB | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 08 / Linha de agua de processo | Rack 1 / Slot 1 / Ch 08 | DI | Dry Contact | XV_413_FB | process water inlet valve position feedback | PNL-PRC-01 | JB-PRC-01 / X2-01
PNL-PRC-01::XV_414_FB | PNL-PRC-01 / Rack 1 / Slot 1 / Ch 09 / Bocal inferior do tanque de mistura | PNL-PRC-01.R1.S1.C9 | DI | Dry Contact | XV_414_FB | mix tank outlet valve position feedback | PNL-PRC-01 | JB-PRC-03 / X1-03
PNL-PRC-01::ALM_418_HORN | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 01 / Sala de processo | R01-S02-CH01 | DO | 24 Vdc Alarm | ALM_418_HORN | Process area alarm horn command | PNL-PRC-01 | JB-PRC-04 / X3-08
PNL-PRC-01::MTR_411_START | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 02 / Topo do tanque de mistura | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | MTR_411_START | mix tank main agitator start command | PNL-PRC-01 | JB-PRC-03 / X2-11 |  | Command released by process interlock.
PNL-PRC-01::PMP_412_START | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 03 / Skid de recirculacao do processo | PNL-PRC-01.R1.S2.C3 | DO | 24 Vdc Run Command | PMP_412_START | process recirculation pump start command | PNL-PRC-01 | JB-PRC-03 / X3-15
PNL-PRC-01::UV_415_ENABLE | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 04 / Skid de sanitizacao | R01-S02-CH04 | DO | 24 Vdc Enable | UV_415_ENABLE | UV module enable command | PNL-PRC-01 | JB-PRC-01 / X3-05
PNL-PRC-01::XV_413_CMD | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 05 / Linha de agua de processo | Rack 1 / Slot 2 / Ch 05 | DO | 24 Vdc Solenoid | XV_413_CMD | process water inlet valve command | PNL-PRC-01 | JB-PRC-04 / X1-16
PNL-PRC-01::XV_414_CMD | PNL-PRC-01 / Rack 1 / Slot 2 / Ch 06 / Bocal inferior do tanque de mistura | PNL-PRC-01.R1.S2.C6 | DO | 24 Vdc Solenoid | XV_414_CMD | mix tank outlet valve command | PNL-PRC-01 | JB-PRC-02 / X3-02
PNL-PRC-01::AIT_407 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 01 / Linha CIP do processo | R02-S01-CH01 | AI | 4-20 mA | AIT_407 | Wash line conductivity transmitter | PNL-PRC-01 | JB-PRC-04 / X2-08 | 0 .. 20 mS/cm
PNL-PRC-01::FIT_406 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 02 / Linha de dosagem do processo | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | FIT_406 | Dosing line flow transmitter | PNL-PRC-01 | JB-PRC-03 / X1-07 | 0 .. 25 m3/h
PNL-PRC-01::LIT_402 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 03 / Tanque de mistura TQ_401 | PNL-PRC-01.R2.S1.C3 | AI | 4-20 mA | LIT_402 | Mix tank level transmitter | PNL-PRC-01 | JB-PRC-03 / X3-03 | 0 .. 100 %
PNL-PRC-01::MTR_411_SPD_FBK | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 04 / Topo do tanque de mistura | R02-S01-CH04 | AI | 4-20 mA | MTR_411_SPD_FBK | mix tank main agitator actual speed feedback | PNL-PRC-01 | JB-PRC-04 / X3-12 | 0 .. 100 %
PNL-PRC-01::PHIT_405 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 05 / Linha de preparo do processo | Rack 2 / Slot 1 / Ch 05 | AI | 4-20 mA | PHIT_405 | Preparation line pH transmitter | PNL-PRC-01 | JB-PRC-02 / X3-06 | 0 .. 14 pH
PNL-PRC-01::PIT_403 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 06 / Manifold de processo | PNL-PRC-01.R2.S1.C6 | AI | 4-20 mA | PIT_403 | Process manifold pressure transmitter | PNL-PRC-01 | JB-PRC-04 / X1-04 | 0 .. 10 bar
PNL-PRC-01::TIT_404 | PNL-PRC-01 / Rack 2 / Slot 1 / Ch 07 / Tanque de mistura TQ_401 | R02-S01-CH07 | AI | 4-20 mA / temp | TIT_404 | Mix tank temperature transmitter | PNL-PRC-01 | JB-PRC-01 / X2-05 | 0 .. 120 °C
PNL-PRC-01::FCV_416_OUT | PNL-PRC-01 / Rack 3 / Slot 1 / Ch 01 / Linha principal de processo | R03-S01-CH01 | AO | 4-20 mA | FCV_416_OUT | Process flow control valve setpoint | PNL-PRC-01 | JB-PRC-02 / X1-06 | 0 .. 100 %
PNL-PRC-01::MTR_411_SPD_REF | PNL-PRC-01 / Rack 3 / Slot 1 / Ch 02 / Topo do tanque de mistura | Rack 3 / Slot 1 / Ch 02 | AO | 4-20 mA | MTR_411_SPD_REF | mix tank main agitator speed setpoint | PNL-PRC-01 | JB-PRC-01 / X1-13 | 0 .. 100 %
PNL-PRC-01::PCV_417_OUT | PNL-PRC-01 / Rack 3 / Slot 1 / Ch 03 / Linha principal de processo | PNL-PRC-01.R3.S1.C3 | AO | 4-20 mA | PCV_417_OUT | Process pressure control valve setpoint | PNL-PRC-01 | JB-PRC-03 / X2-07 | 0 .. 100 %
PNL-PRC-01::SPARE_AO_PRC_02 | PNL-PRC-01 / Rack 3 / Slot 1 / Ch 04 / Sala de processo / plataforma principal | R03-S01-CH04 | SPARE | Reserved AO8 | SPARE_AO_PRC_02 | Reserved analog output on process panel | PNL-PRC-01 | JB-PRC-02 / X2-10 |  | Provisioned for future extra dosing loop.
PNL-RCV-01::CV_111_FLT | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 01 / Base da moega rodoviaria | R01-S01-CH01 | DI | Aux Contact | CV_111_FLT | receiving discharge screw conveyor fault feedback | PNL-RCV-01 | JB-RCV-03 / X1-07 |  | Signal sourced from the drive.
PNL-RCV-01::CV_111_RUN | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 02 / Base da moega rodoviaria | Rack 1 / Slot 1 / Ch 02 | DI | Aux Contact | CV_111_RUN | receiving discharge screw conveyor running feedback | PNL-RCV-01 | JB-RCV-02 / X3-06
PNL-RCV-01::LSH_101 | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 03 / Moega rodoviaria | PNL-RCV-01.R1.S1.C3 | DI | Dry Contact | LSH_101 | Truck hopper high level switch | PNL-RCV-01 | JB-RCV-03 / X3-03 |  | Field set point adjusted to 85%.
PNL-RCV-01::LSL_101 | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 04 / Moega rodoviaria | R01-S01-CH04 | DI | Dry Contact | LSL_101 | Truck hopper low level switch | PNL-RCV-01 | JB-RCV-04 / X1-04
PNL-RCV-01::MTR_112_RUN | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 05 / Cobertura do filtro de mangas | Rack 1 / Slot 1 / Ch 05 | DI | Aux Contact | MTR_112_RUN | receiving dust collector fan running feedback | PNL-RCV-01 | JB-RCV-03 / X2-11
PNL-RCV-01::SPARE_DI_RCV_01 | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 06 / Recebimento norte / moega rodoviaria | PNL-RCV-01.R1.S1.C6 | SPARE | Reserved DI16 | SPARE_DI_RCV_01 | Reserved digital input on receiving panel | PNL-RCV-01 | JB-RCV-03 / X1-03 |  | Reserved for future level switch.
PNL-RCV-01::XV_101_FB | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 07 / Fosso rodoviario / extremidade norte | R01-S01-CH07 | DI | Dry Contact | XV_101_FB | truck pit discharge gate position feedback | PNL-RCV-01 | JB-RCV-02 / X2-02
PNL-RCV-01::YV_115_FB | PNL-RCV-01 / Rack 1 / Slot 1 / Ch 08 / Bica de amostragem do recebimento | Rack 1 / Slot 1 / Ch 08 | DI | Dry Contact | YV_115_FB | sampling diverter valve position feedback | PNL-RCV-01 | JB-RCV-04 / X1-16
PNL-RCV-01::CV_111_START | PNL-RCV-01 / Rack 1 / Slot 2 / Ch 01 / Base da moega rodoviaria | R01-S02-CH01 | DO | 24 Vdc Run Command | CV_111_START | receiving discharge screw conveyor start command | PNL-RCV-01 | JB-RCV-04 / X2-08 |  | Command released by process interlock.
PNL-RCV-01::MTR_112_START | PNL-RCV-01 / Rack 1 / Slot 2 / Ch 02 / Cobertura do filtro de mangas | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | MTR_112_START | receiving dust collector fan start command | PNL-RCV-01 | JB-RCV-04 / X3-12
PNL-RCV-01::PMP_117_START | PNL-RCV-01 / Rack 1 / Slot 2 / Ch 03 / Skid de lavagem do piso | PNL-RCV-01.R1.S2.C3 | DO | 24 Vdc Run Command | PMP_117_START | Wash water pump start command | PNL-RCV-01 | JB-RCV-02 / X3-02
PNL-RCV-01::XV_101_CMD | PNL-RCV-01 / Rack 1 / Slot 2 / Ch 04 / Fosso rodoviario / extremidade norte | R01-S02-CH04 | DO | 24 Vdc Solenoid | XV_101_CMD | truck pit discharge gate command | PNL-RCV-01 | JB-RCV-01 / X1-01
PNL-RCV-01::YV_115_CMD | PNL-RCV-01 / Rack 1 / Slot 2 / Ch 05 / Bica de amostragem do recebimento | Rack 1 / Slot 2 / Ch 05 | DO | 24 Vdc Solenoid | YV_115_CMD | sampling diverter valve command | PNL-RCV-01 | JB-RCV-03 / X3-15
PNL-RCV-01::CV_111_SPD_FBK | PNL-RCV-01 / Rack 2 / Slot 1 / Ch 01 / Base da moega rodoviaria | R02-S01-CH01 | AI | 4-20 mA | CV_111_SPD_FBK | receiving discharge screw conveyor actual speed feedback | PNL-RCV-01 | JB-RCV-01 / X3-09 | 0 .. 100 %
PNL-RCV-01::FIT_114 | PNL-RCV-01 / Rack 2 / Slot 1 / Ch 02 / Calha de descarga do recebimento | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | FIT_114 | Receiving discharge flow transmitter | PNL-RCV-01 | JB-RCV-02 / X2-14 | 0 .. 60 t/h
PNL-RCV-01::LIT_101 | PNL-RCV-01 / Rack 2 / Slot 1 / Ch 03 / Moega rodoviaria | PNL-RCV-01.R2.S1.C3 | AI | 4-20 mA | LIT_101 | Truck hopper level transmitter | PNL-RCV-01 | JB-RCV-01 / X2-05 | 0 .. 100 % | Scale adjusted for normal operation between 10% and 90%.
PNL-RCV-01::PIT_113 | PNL-RCV-01 / Rack 2 / Slot 1 / Ch 04 / Linha de ar de fluidizacao | R02-S01-CH04 | AI | 4-20 mA | PIT_113 | Fluidization line pressure transmitter | PNL-RCV-01 | JB-RCV-01 / X1-13 | 0 .. 6 bar
PNL-RCV-01::CV_111_SPD_REF | PNL-RCV-01 / Rack 3 / Slot 1 / Ch 01 / Base da moega rodoviaria | R03-S01-CH01 | AO | 4-20 mA | CV_111_SPD_REF | receiving discharge screw conveyor speed setpoint | PNL-RCV-01 | JB-RCV-02 / X1-10 | 0 .. 100 %
PNL-RCV-01::FCV_116_OUT | PNL-RCV-01 / Rack 3 / Slot 1 / Ch 02 / Linha de umectacao do recebimento | Rack 3 / Slot 1 / Ch 02 | AO | 4-20 mA | FCV_116_OUT | Water dosing valve setpoint | PNL-RCV-01 | JB-RCV-01 / X2-01 | 0 .. 100 %
PNL-UTL-01::COMP_601_FLT | PNL-UTL-01 / Rack 1 / Slot 1 / Ch 01 / Casa de utilidades / skid do compressor | R01-S01-CH01 | DI | Aux Contact | COMP_601_FLT | Main compressor fault feedback | PNL-UTL-01 | JB-UTL-02 / X2-02
PNL-UTL-01::COMP_601_RUN | PNL-UTL-01 / Rack 1 / Slot 1 / Ch 02 / Casa de utilidades / skid do compressor | Rack 1 / Slot 1 / Ch 02 | DI | Aux Contact | COMP_601_RUN | Main compressor running feedback | PNL-UTL-01 | JB-UTL-01 / X1-01
PNL-UTL-01::PMP_606_RUN | PNL-UTL-01 / Rack 1 / Slot 1 / Ch 03 / Skid da torre de resfriamento | PNL-UTL-01.R1.S1.C3 | DI | Aux Contact | PMP_606_RUN | cooling tower recirculation pump running feedback | PNL-UTL-01 | JB-UTL-01 / X3-09
PNL-UTL-01::XV_605_FB | PNL-UTL-01 / Rack 1 / Slot 1 / Ch 04 / Header de ar comprimido | R01-S01-CH04 | DI | Dry Contact | XV_605_FB | air header isolation valve position feedback | PNL-UTL-01 | JB-UTL-04 / X2-08
PNL-UTL-01::COMP_601_START | PNL-UTL-01 / Rack 1 / Slot 2 / Ch 01 / Casa de utilidades / skid do compressor | R01-S02-CH01 | DO | 24 Vdc Run Command | COMP_601_START | Main compressor start command | PNL-UTL-01 | JB-UTL-03 / X3-03
PNL-UTL-01::PMP_606_START | PNL-UTL-01 / Rack 1 / Slot 2 / Ch 02 / Skid da torre de resfriamento | Rack 1 / Slot 2 / Ch 02 | DO | 24 Vdc Run Command | PMP_606_START | cooling tower recirculation pump start command | PNL-UTL-01 | JB-UTL-02 / X1-10
PNL-UTL-01::XV_605_CMD | PNL-UTL-01 / Rack 1 / Slot 2 / Ch 03 / Header de ar comprimido | PNL-UTL-01.R1.S2.C3 | DO | 24 Vdc Solenoid | XV_605_CMD | air header isolation valve command | PNL-UTL-01 | JB-UTL-03 / X1-07
PNL-UTL-01::FIT_603 | PNL-UTL-01 / Rack 2 / Slot 1 / Ch 01 / Linha de agua industrial | R02-S01-CH01 | AI | 4-20 mA | FIT_603 | Industrial water flow transmitter | PNL-UTL-01 | JB-UTL-01 / X2-05 | 0 .. 40 m3/h
PNL-UTL-01::PIT_602 | PNL-UTL-01 / Rack 2 / Slot 1 / Ch 02 / Header principal de ar comprimido | Rack 2 / Slot 1 / Ch 02 | AI | 4-20 mA | PIT_602 | Compressed air header pressure transmitter | PNL-UTL-01 | JB-UTL-04 / X1-04 | 0 .. 10 bar
PNL-UTL-01::SPARE_AI_UTL_01 | PNL-UTL-01 / Rack 2 / Slot 1 / Ch 03 / Casa de utilidades / skid de servicos | PNL-UTL-01.R2.S1.C3 | SPARE | Reserved AI8 | SPARE_AI_UTL_01 | Reserved analog input on utilities panel | PNL-UTL-01 | JB-UTL-04 / X3-12 |  | Reserved for future dew point transmitter.
PNL-UTL-01::TIT_604 | PNL-UTL-01 / Rack 2 / Slot 1 / Ch 04 / Linha de agua gelada | R02-S01-CH04 | AI | 4-20 mA / temp | TIT_604 | Chilled water line temperature transmitter | PNL-UTL-01 | JB-UTL-02 / X3-06 | 0 .. 30 °C
PNL-UTL-01::PCV_607_OUT | PNL-UTL-01 / Rack 3 / Slot 1 / Ch 01 / Header de ar comprimido | R03-S01-CH01 | AO | 4-20 mA | PCV_607_OUT | Air pressure control valve setpoint | PNL-UTL-01 | JB-UTL-03 / X2-11 | 0 .. 100 %

## Index
Panel | Area | Racks | Points | Primary Sheet
MCC-TRN-01 | Transporte | 1,2,3 | 25 | refer to data tabs
PNL-BAG-01 | Ensacadeira | 1,2,3 | 16 | refer to data tabs
PNL-MOG-01 | Moega | 1,2,3 | 22 | refer to data tabs
PNL-PRC-01 | Processo | 1,2,3 | 26 | refer to data tabs
PNL-RCV-01 | Recebimento | 1,2,3 | 19 | refer to data tabs
PNL-UTL-01 | Utilidades | 1,2,3 | 12 | refer to data tabs

## Rack Map
Panel | Rack | Points | DI | DO | AI | AO | SPARE
MCC-TRN-01 | 1 | 16 | 8 | 7 | 0 | 0 | 1
MCC-TRN-01 | 2 | 6 | 0 | 0 | 5 | 0 | 1
MCC-TRN-01 | 3 | 3 | 0 | 0 | 0 | 3 | 0
PNL-BAG-01 | 1 | 11 | 5 | 5 | 0 | 0 | 1
PNL-BAG-01 | 2 | 4 | 0 | 0 | 4 | 0 | 0
PNL-BAG-01 | 3 | 1 | 0 | 0 | 0 | 1 | 0
PNL-MOG-01 | 1 | 14 | 8 | 6 | 0 | 0 | 0
PNL-MOG-01 | 2 | 6 | 0 | 0 | 5 | 0 | 1
PNL-MOG-01 | 3 | 2 | 0 | 0 | 0 | 2 | 0
PNL-PRC-01 | 1 | 15 | 8 | 6 | 0 | 0 | 1
PNL-PRC-01 | 2 | 7 | 0 | 0 | 7 | 0 | 0
PNL-PRC-01 | 3 | 4 | 0 | 0 | 0 | 3 | 1
PNL-RCV-01 | 1 | 13 | 7 | 5 | 0 | 0 | 1
PNL-RCV-01 | 2 | 4 | 0 | 0 | 4 | 0 | 0
PNL-RCV-01 | 3 | 2 | 0 | 0 | 0 | 2 | 0
PNL-UTL-01 | 1 | 7 | 4 | 3 | 0 | 0 | 0
PNL-UTL-01 | 2 | 4 | 0 | 0 | 3 | 0 | 1
PNL-UTL-01 | 3 | 1 | 0 | 0 | 0 | 1 | 0